## APK Campus
Supply and Installation of UPS Systems
Protection Service Gates
APK Gate 1 ¦ APK Gate 1A ¦APK Gate 6 ¦ APK Gate 2
Item no |  | Unit | QTY | Rate | Total amount
PRELIMINARY AND GENERAL
GENERAL
The contractor shall carry out the whole work with as little mess and noise as possible and with a minimum of disturbance to adjoining premises and their tenants. He shall provide proper protection and provide and erect any temporary tarpaulins that may be necessary during the progress of the works, all to the satisfaction of the UJ agent, and remove when directed.
All inferior work shall, on indication by the Department’s inspecting officers, immediately be removed and rectified by and at the expense of the Contractor
Wherever applicable the material is to comply with the relevant South African Bureau of Standards or specifications
Protection of adjoining structures
SCOPE
Supply and Install UPS Systems to access gates at various UJ APK Campus
UPS SYSTEM
1 | Supply of 6KVA ON-LINE UPS 0.9PF 5.4K (IP66) single phase in and out | no | 3
2 | Supply of BATTERY 12V 40AH GEL TYPE | no | 36
CABINETS
3 | Supply of 25U CABINET 600 X 800, with Power | no | 3
| Security cage steel to protect UPS against theft | no | 3
PARTS
4 | Provision of 8-way distribution board with main breaker and 4 outgoing feeder breakers | no | 3
5 | Delivery | Item | 3
6 | Installation | Item | 3
CABLES
7 | 16mm squared 4 core PVC cable | m | 80
ENCLOSURE
8 | Supply of External Enclosure 1.6m X 1.2m (IP66) | no | 3
EXCAVATIONS
9 | Excavations 0.5 m deep and 100 m width | m | 10
| concrete plinth/stand for UPS (300mm depth and wide) | Ea | 3
RESOURCES
10 | Labour | lot
CERTIFCATES
11 | Issue COC | Ea | 4
CONTINGENCY
| Allow a contingency amount at 5% of the contract amount to be used as directed by the Principal Agent | Item | 5%
SUB TOTAL…............................................................................................................................................................................................. |  |  |  |  | R
VAT @ 15% ……………………………………………………………………………………………………………………......................................................... |  |  |  |  | R
TOTAL …………………………………………………………………………………………………………………………………….......................... |  |  |  |  | R

## APB Campus
Supply and Installation of UPS Systems
Protection Service Gates
APB Gate G Sekwana ¦ APB Canary Gate
Item no |  | Unit | QTY | Rate | Total amount
PRELIMINARY AND GENERAL
GENERAL
The contractor shall carry out the whole work with as little mess and noise as possible and with a minimum of disturbance to adjoining premises and their tenants. He shall provide proper protection and provide and erect any temporary tarpaulins that may be necessary during the progress of the works, all to the satisfaction of the UJ agent, and remove when directed.
All inferior work shall, on indication by the Department’s inspecting officers, immediately be removed and rectified by and at the expense of the Contractor
Wherever applicable the material is to comply with the relevant South African Bureau of Standards or specifications
Protection of adjoining structures
SCOPE
Supply and Install UPS Systems to access gates at various UJ APB campus
UPS SYSTEM
1 | Supply of 6KVA ON-LINE UPS 0.9PF 5.4K (IP66) single phase in and out | no | 4
2 | Supply of BATTERY 12V 40AH GEL TYPE | no | 64
CABINETS
3 | Supply of 25U CABINET 600 X 800, with Power | no | 4
| Security cage steel to protect UPS against theft | no | 4
PARTS
4 | Provision of 8-way distribution board with main breaker and 4 outgoing feeder breakers | no | 4
5 | Delivery | Item | 4
6 | Installation | Item | 2
CABLES
7 | 16mm squared 4 core PVC cable | m | 40
ENCLOSURE
8 | Supply of External Enclosure 1.6m X 1.2m (IP66) | no | 4
EXCAVATIONS
9 | Excavations 0.5 m deep and 100 m width | m | 20
| concrete plinth/stand for UPS (300mm depth and wide) | Ea | 4
RESOURCES
10 | Labour | lot
CERTIFCATES
11 | Issue COC | Ea | 4
CONTINGENCY
| Allow a contingency amount at 5% of the contract amount to be used as directed by the Principal Agent | Item | 5%
SUB TOTAL…............................................................................................................................................................................................. |  |  |  |  | R
VAT @ 15% ……………………………………………………………………………………………………………………......................................................... |  |  |  |  | R
TOTAL …………………………………………………………………………………………………………………………………….......................... |  |  |  |  | R

## DFC Campus
Supply and Installation of UPS Systems
Protection Service Gates
DFC Main Gate ¦ DFC Sherwell Gate ¦DFC Nind Str Gate
Item no |  | Unit | QTY | Rate | Total amount
PRELIMINARY AND GENERAL
GENERAL
The contractor shall carry out the whole work with as little mess and noise as possible and with a minimum of disturbance to adjoining premises and their tenants. He shall provide proper protection and provide and erect any temporary tarpaulins that may be necessary during the progress of the works, all to the satisfaction of the UJ agent, and remove when directed.
All inferior work shall, on indication by the Department’s inspecting officers, immediately be removed and rectified by and at the expense of the Contractor
Wherever applicable the material is to comply with the relevant South African Bureau of Standards or specifications
Protection of adjoining structures
SCOPE
Supply and Install UPS Systems to access gates at various UJ DFC Campus
UPS SYSTEM
1 | Supply of 6KVA ON-LINE UPS 0.9PF 5.4K (IP66) single phase in and out | no | 1
2 | Supply of BATTERY 12V 40AH GEL TYPE | no | 16
CABINETS
3 | Supply of 25U CABINET 600 X 800, with Power | no | 1
| Security cage steel to prevent UPS against theft | no | 1
PARTS
4 | Provision of 8-way distribution board with main breaker and 4 outgoing feeder breakers | no | 1
5 | Delivery | Item | 1
6 | Installation | Item | 1
CABLES
7 | 16mm squared 4 core PVC cable | m | 20
ENCLOSURE
8 | Supply of External Enclosure 1.6m X 1.2m (IP66) | no | 1
EXCAVATIONS
9 | Excavations 0.5 m deep and 100 m width | m | 15
| concrete plinth/stand for UPS (300mm depth and wide) | Ea | 1
RESOURCES
10 | Labour | lot
CERTIFCATES
11 | Issue COC | Ea | 1
CONTINGENCY
| Allow a contingency amount at 5% of the contract amount to be used as directed by the Principal Agent | Item | 5%
SUB TOTAL…............................................................................................................................................................................................. |  |  |  |  | R
VAT @ 15% ……………………………………………………………………………………………………………………......................................................... |  |  |  |  | R
TOTAL …………………………………………………………………………………………………………………………………….......................... |  |  |  |  | R

## SWC Campus
Supply and Installation of UPS Systems
Protection Service Gates
Soweto Main Gate
Item no |  | Unit | QTY | Rate | Total amount
PRELIMINARY AND GENERAL
GENERAL
The contractor shall carry out the whole work with as little mess and noise as possible and with a minimum of disturbance to adjoining premises and their tenants. He shall provide proper protection and provide and erect any temporary tarpaulins that may be necessary during the progress of the works, all to the satisfaction of the UJ agent, and remove when directed.
All inferior work shall, on indication by the Department’s inspecting officers, immediately be removed and rectified by and at the expense of the Contractor
Wherever applicable the material is to comply with the relevant South African Bureau of Standards or specifications
Protection of adjoining structures
SCOPE
Supply and Install UPS Systems to access gates at various UJ SWC Campus
UPS SYSTEM
1 | Supply of 6KVA ON-LINE UPS 0.9PF 5.4K (IP66) single phase in and out | no | 1
2 | Supply of BATTERY 12V 40AH GEL TYPE | no | 16
CABINETS
3 | Supply of 25U CABINET 600 X 800, with Power | no | 1
| Security cage steel to protect UPS against theft | no | 1
PARTS
4 | Provision of 8-way distribution board with main breaker and 4 outgoing feeder breakers | no | 1
5 | Delivery | Item | 1
6 | Installation | Item | 1
CABLES
7 | 16mm squared 4 core PVC cable | m | 20
ENCLOSURE
8 | Supply of External Enclosure 1.6m X 1.2m (IP66) | no | 1
| Stainless steel cage | item | 1
| concrete plinth/stand for UPS (300mm depth and wide) | Ea | 1
EXCAVATIONS
9 | Excavations 0.5 m deep and 100 m width | m | 7
RESOURCES
10 | Labour | lot
SERVICE AND MAINTANCE
11 | Warranty (years) |  | 1
CERTIFCATES
12 | Issue COC | Ea | 1
CONTINGENCY
| Allow a contingency amount at 5% of the contract amount to be used as directed by the Principal Agent | Item | 5%
SUB TOTAL…............................................................................................................................................................................................. |  |  |  |  | R
VAT @ 15% ……………………………………………………………………………………………………………………......................................................... |  |  |  |  | R
TOTAL …………………………………………………………………………………………………………………………………….......................... |  |  |  |  | R